# Industrial Energy Dispatch – Technical Manual

## 1. Model objective

The model finds the lowest-cost 24-hour operating schedule for an industrial energy system consisting of a CHP unit, a gas boiler, photovoltaic generation, a battery, and the power grid. In every hour, both the electrical and thermal balances as well as the technical equipment constraints must be satisfied.

Mathematically, this is a MILP (Mixed-Integer Linear Programming):

minxcTx

subject to

lb≤Ax≤ub,

lower≤x≤upper,

with some components of x being binary.

## 2. Decision variables

For each hour t=0,…,23 the model contains mainly:

- FCHP,t – CHP fuel input,

- PCHP,t – CHP electrical output,

- QCHP,t – CHP thermal output,

- FB,t – boiler fuel input,

- PIMP,t,PEXP,t – electricity import and export,

- PCHG,t,PDIS,t – battery charging and discharging,

- SOCt – battery state of charge,

- ONt∈{0,1} – CHP on/off state,

- STARTt∈{0,1} – CHP startup indicator,

- SEGt,s∈{0,1} – selected segment of the piecewise characteristic,

- αt,s∈0,1 – position within the segment.

All variables are stored in one long vector x.

## 3. Piecewise-linear CHP characteristic

The underlying physical model uses nonlinear efficiency, for example

PF=ηelFF,  QF=ηthFF.

To use MILP, the curve is approximated by several linear segments. For known breakpoints, we have the triplets

fs,ps,qs.

Four points define three segments.

### Segment selection

For each hour,

s​SEGt,s=ONt.

If ONt=0, all segment variables are zero. If ONt=1, exactly one binary SEGt,s must be equal to 1.

In Python, this relationship is created as one row of matrix A: the coefficients of the three corresponding SEG are +1, the coefficient of ONt is -1 and all other coefficients are zero.

### Position within the segment

For each segment:

0≤αt,s≤SEGt,s.

If the segment is inactive, SEGt,s=0 and therefore αt,s=0. Only in the active segment can α take a value between 0 and 1.

### Interpolation of fuel, electricity, and heat

The same SEG and the same α determine all three quantities:

FCHP,t=s​fsSEGt,s+fs+1-fsαt,s,

PCHP,t=s​psSEGt,s+ps+1-psαt,s,

QCHP,t=s​qsSEGt,s+qs+1-qsαt,s.

This ensures that fuel input, electrical output, and thermal output represent one consistent operating point on the same part of the approximated characteristic.

## 4. What a matrix row looks like

For one hour, consider the simplified local vector

xlocal=F,P,Q,ON,y0,y1,y2,α0,α1,α2T.

The equation

y0+y1+y2-ON=0

has the row

0,0,0,-1,1,1,1,0,0,0.

The inequality

α1-y1≤0

has the row

0,0,0,0,0,-1,0,0,1,0,

with lower bound -∞ and upper bound 0.

The fuel interpolation has the row

1,0,0,0,-f0,-f1,-f2,-Δf0,-Δf1,-Δf2,

with right-hand side 0.

Each a = np.zeros(n) therefore creates a new row of A and assigning values to several indices sets its nonzero coefficients.

## 5. Energy balances

Heat balance:

QCHP,t+ηBFB,t=Dheat,t.

Electricity balance:

PCHP,t+PVt+PIMP,t-PEXP,t+PDIS,t-PCHG,t=Del,t.

The piecewise block only determines which values of F,P,Q are feasible for the CHP. The balances and prices then determine which operating point is optimal.

## 6. Battery

The state-of-charge dynamics are

SOCt=SOCt-1+ηcPCHG,t-PDIS,tηd.

The model also requires equal initial and final SOC so that costs cannot be artificially reduced by emptying the battery at the end of the horizon.

## 7. CHP ramp limit

The maximum change in CHP fuel input between two consecutive hours is

FCHP,t-FCHP,t-1≤R.

Linear equivalent:

-R≤FCHP,t-FCHP,t-1≤R.

The corresponding matrix row has coefficient -1 at FCHP,t-1, +1 at FCHP,t and zeros elsewhere. The lower bound is -R, and the upper bound is R.

The ramp limit is unrelated to the width of the piecewise segments. The segments approximate the static equipment characteristic; the ramp constraint limits the change over time between hours.

## 8. Startup

The transition from off to on can be captured, for example, by the constraint

STARTt≥ONt-ONt-1.

Because STARTt has a positive cost in the objective, the solver will not set it to 1 unless necessary.

## 9. Objective function

The model minimizes

t​cgasFCHP,t+FB,t+cbuy,tPIMP,t-csell,tPEXP,t+ccyclePCHG,t+PDIS,t+cstartSTARTt.

The coefficients of this function form vector c. After optimization, result.fun is the minimum value found for cTx.

## 10. How the matrix is assembled in Python

Schematically:

a = np.zeros(n)                # new row of matrix A
a[index_1] = 1.0              # coefficient of one variable
a[index_2] = -1.0             # coefficient of another variable
add_constraint(a, low, high)  # low <= a^T x <= high

A = np.vstack(rows)
constraints = LinearConstraint(A, np.array(lows), np.array(highs))

Matrix A is an ordinary linear operator x↦Ax. The fact that some rows represent inequalities does not change its linearity; only the allowed intervals differ from row to row lbi,ubi.

## 11. What milp()

The solver finds all components of x simultaneously. There is no sequential calculation of “first F, then P, then Q”. The equations only enforce consistency among them.

After piecewise linearization, there is no need for brentq(), because the optimization problem itself contains only linear equations and inequalities plus binary variables.

## 12. Quality of the piecewise approximation

The MILP solver does not check how well the piecewise curve approximates the original nonlinear characteristic. For the solver, the supplied approximation is the exact model.

The approximation quality should be checked separately, for example using

eabs=maxFftrueF-fPWLF,

or the relative error

erel=maxFftrueF-fPWLFmaxftrueF,ε.

If the error is too large, additional breakpoints can be added. A more advanced option is adaptive piecewise-linear approximation: intervals are refined where the error or curvature is greatest until the chosen tolerance is satisfied.

## 13. Result validation

After optimization, the energy balances, SOC, grid limits, and ramp limit are checked again. assert acts as a quick safeguard: if an invariant does not hold, Python raises AssertionError.

## 14. What is simplified in the model

- the piecewise CHP characteristic is an approximation,

- the boiler may use constant efficiency,

- the time step is one hour,

- detailed thermodynamics, pressure levels, maintenance, and uncertainty are not modeled,

- input profiles and prices are illustrative.

## 15. Short interview explanation

The model optimizes a 24-hour dispatch of a CHP unit, boiler, battery, and power grid. The nonlinear CHP characteristic is replaced by a piecewise-linear approximation, so the full problem remains a MILP. Binary variables select the active segment and the continuous variable α determines the position within the segment. The same SEG and α simultaneously determine fuel input, electrical output, and thermal output. The model also respects energy balances, ramping, startup logic, and battery SOC while minimizing total operating cost.

## 16. Program output

A normal run produces three types of output: a console summary, a CSV file with the complete hourly dispatch, and four diagnostic/result figures. The numerical values below are an example for the bundled illustrative profiles and parameters; they will change if the input data or equipment parameters are modified.

### 16.1 Console summary

- Baseline daily cost: Cost of the benchmark strategy in which the boiler supplies the heat demand and the grid supplies net electricity demand.

- Optimized daily cost: Minimum objective value returned by the MILP for the optimized 24-hour dispatch.

- Daily saving: Baseline daily cost minus optimized daily cost.

- Saving [%]: Daily saving divided by baseline daily cost.

- CHP startups: Number of hours in which the binary START variable is active; this counts transitions from off to on.

- Peak grid import: Maximum hourly electricity import from the grid [MW].

- Peak grid export: Maximum hourly electricity export to the grid [MW].

Example output for the bundled demonstration data:

| Metric | Example value |
| --- | --- |
| Baseline daily cost | 21,571.39 EUR |
| Optimized daily cost | 14,170.91 EUR |
| Daily saving | 7,400.48 EUR |
| Saving | 34.31 % |
| CHP startups | 1 |
| Peak grid import | 2.88 MW |
| Peak grid export | 0.00 MW |

The script also prints the CHP piecewise operating points. Each row contains load fraction, fuel input, electrical efficiency, thermal efficiency, electrical output and thermal output. These points are the breakpoints used by the MILP piecewise-linear formulation.

### 16.2 CSV output

The complete hourly solution is saved as dispatch_results_piecewise.csv. One row corresponds to one hour. The most important columns are:

| Column | Meaning |
| --- | --- |
| hour | Hour index 0–23. |
| electric_demand | Electrical demand [MW]. |
| heat_demand | Heat demand [MW]. |
| pv | Available photovoltaic generation [MW]. |
| buy_price | Grid electricity purchase price [EUR/MWh]. |
| sell_price | Grid electricity export price [EUR/MWh]. |
| chp_on | Binary optimized CHP on/off state. |
| chp_start | Binary optimized CHP startup indicator. |
| chp_fuel | Optimized CHP fuel input [MW of fuel-energy input]. |
| chp_el | Optimized CHP electrical output [MW]. |
| chp_heat | Optimized CHP thermal output [MW]. |
| chp_eta_el | Effective electrical efficiency reconstructed from optimized output/fuel. |
| chp_eta_th | Effective thermal efficiency reconstructed from optimized output/fuel. |
| boiler_fuel | Optimized boiler fuel input [MW of fuel-energy input]. |
| boiler_heat | Optimized boiler heat output [MW]. |
| grid_import | Electricity imported from the grid [MW]. |
| grid_export | Electricity exported to the grid [MW]; stored as a non-negative magnitude. |
| battery_charge | Battery charging power [MW]. |
| battery_discharge | Battery discharging power [MW]. |
| battery_soc | Battery state of charge [MWh]. |
| hourly_cost | Objective contribution of the hour [EUR]. |

## 17. Figures

The figures are diagnostic as well as presentational: they show whether the optimized dispatch is physically interpretable and how the main decisions respond to demand, prices and the CHP performance characteristic.

### 17.1 Electricity dispatch

The first figure shows electrical demand together with CHP electricity production, PV generation, grid import and grid export. The y-axis is electrical power [MW]. Grid export is plotted below zero only to make the direction of power flow visually obvious; in the result table grid_export is stored as a non-negative export magnitude. The electrical balance is enforced for every hour, so generation plus net grid exchange and battery discharge/charge must match demand.

### 17.2 Heat dispatch

The second figure shows heat demand, CHP thermal output and boiler thermal output in MW. Their hourly sum must equal the heat demand. The plot therefore makes the heat balance and the division of load between CHP and boiler immediately visible.

### 17.3 Electricity price and battery state

The third figure deliberately combines two related but dimensionally different quantities. Electricity purchase price uses the left y-axis [EUR/MWh], while battery state of charge uses the right y-axis [MWh]. Separate y-axes are essential because the quantities have different units and very different numerical scales. The common time axis makes it possible to inspect whether battery operation is consistent with the price signal. SOC is an energy state, not a power flow; charging and discharging power are available in the CSV output if a more detailed battery plot is desired.

### 17.4 CHP performance curves

The fourth figure compares the original nonlinear CHP electrical and thermal output curves with the piecewise-linear curves actually supplied to the MILP. The x-axis is CHP fuel input [MW of fuel-energy input] and the y-axis is CHP output [MW]. Markers show the selected breakpoints (25 %, 50 %, 75 % and 100 % load). Straight lines between adjacent breakpoints are the MILP approximation. This figure is therefore a direct visual check of the modeling approximation rather than a dispatch result.

The MILP solver itself does not assess whether the piecewise approximation is sufficiently accurate. If tighter fidelity is required, the nonlinear and piecewise curves should be compared quantitatively and additional breakpoints introduced where the approximation error is too large.

## 18. Units and interpretation

| Quantity | Unit |
| --- | --- |
| Power flows and fuel-energy input | MW |
| Battery state of charge | MWh |
| Electricity prices | EUR/MWh |
| Hourly and daily costs | EUR |
| Time step | 1 hour |

Because the time step is one hour, a constant power of 1 MW over one model interval corresponds numerically to 1 MWh of energy over that interval. The distinction is still kept in the labels: interval power flows are shown in MW, while stored battery energy is shown in MWh.